Enos Home Inspections

Building Inspection Report

123 Knowwear Lane, Schenectady NY 12309

Inspection Date:

March 1,2015

Prepared For:

Clients Name

Sample Report

Prepared By:

Enos Home Inspections

1A Concord Dr

Schenectady,NY,12309

5183657211

Enoshomeinspections@gmail.com

Report Number:

0224151

Inspector:

Keith Enos

Lic#16000055677

© 2015 Enos Home Inspections

# Report Overview

## THE HOUSE IN PERSPECTIVE

This is an average quality home.  As with all homes, ongoing maintenance is required and improvements to the systems of the home will be needed over time.  The improvements that are recommended in this report are not considered unusual for a home of this age and location.  Please remember that there is no such thing as a perfect home.

## CONVENTIONS USED IN THIS REPORT

For your convenience, the following conventions have been used in this report.

Major Concern: a system or component which is considered significantly deficient or is unsafe. Significant deficiencies need to be corrected and, except for some safety items, are likely to involve significant expense.

Safety Issue:  denotes a condition that is unsafe and in need of prompt attention.

Repair: denotes a system or component which is missing or which needs corrective action to assure proper and reliable function.

Improve:  denotes improvements which are recommended but not required.

Monitor:  denotes a system or component needing further investigation and/or monitoring in order to determine if repairs are necessary.

Deferred Cost: denotes items that have reached or are reaching their normal life expectancy or show indications that they may require repair or replacement anytime during the next five (5) years.

Please note that those observations listed under “Discretionary Improvements” are not essential repairs, but represent logical long term improvements.

- For the purpose of this report, it is assumed that the house faces north.

## IMPROVEMENT RECOMMENDATION HIGHLIGHTS / summary

The following is a synopsis of the potentially significant improvements that should be budgeted for over the short term.  Other significant improvements, outside the scope of this inspection, may also be necessary.  Please refer to the body of this report for further details on these and other recommendations.

Limitations

- The air conditioning system could not be tested as the outdoor temperature was at or below 65 degrees F.

Major Concerns

- Major Concern, Repair, Safety Issue:  The masonry chimney shows evidence of substantial deterioration. Rebuilding is needed to assure a safe and functional flue. The roof is actively leaking near chimney and needs to be evaluated by a contractor.

Safety Issues

- Safety Issue:    The main panel cover plate (sometimes called the “Dead Front”) is loose. It should be replaced.

- Safety Issue:    Circuits within the main distribution panel that are doubled up (referred to as “double taps”) should be separated. Each circuit should be served by a separate fuse or breaker.

- Safety Issue:  The panel has homemade junction needs to be evaluated by a contractor.

- Safety Issue:  All junction boxes should be fitted with cover plates, in order to protect the wire connections.

- Monitor: Safety Issue:   Insulation on the boiler and/or distribution piping may contain asbestos. This can only be verified by laboratory analysis. The Environmental Protection Agency (E.P.A.) reports that asbestos represents a health hazard if “friable” (damaged, crumbling, or in any state that allows the release of fibers). If replacement of the boiler necessitates the removal of the asbestos containing insulation, a specialist should be engaged. If any sections of this insulation are indeed friable, or become friable over time, a specialist should be engaged. Further guidance is available from the E.P.A. Due to the age of construction, there may be other materials within the home that contain asbestos but are not identified by this inspection report.

Repair Items

- Repair:  A rain cap and vermin screen should be installed on the masonry chimney and the chimney flue should be checked for damage. Damaged flues can be unsafe.

- Repair:  The exterior brickwork should be re-pointed (replacement of the mortar between the bricks) to prevent further deterioration.

- Repair:  No hot water on second floor.

- Repair:  The windows require caulking at front of house..

Improvement items

- Major Concern, Monitor:  the detached garage is a low quality structure. With the exception of keeping the roof watertight and having functional gutters for roof water, it may not be worth investing in repairs. Rebuilding would be the better long term approach.

- Repair:  The heating system requires service. This should be a regular maintenance item to assure safe, reliable heat.

Items to Monitor

- Monitor:  The driveway drain is  marginally adequate. Its performance should be carefully monitored during heavy rains. Care should be taken to maintain this drain free of debris. If problems develop, a large drain spanning the width of the driveway would be preferred. Drive runoff must be directed away from the building to avoid water entry/damage.

deferred cost Items

- Deferred Cost Item:  The water heater is an old unit that may be approaching the end of its useful life. It would be wise to budget for a new unit. One cannot predict with certainty when replacement will become necessary.

## THE SCOPE OF THE INSPECTION

All components designated for inspection in the ASHI( Standards of Practice are inspected, except as may be noted in the “Limitations of Inspection” sections within this report.

It is the goal of the inspection to put a home buyer in a better position to make a buying decision.  Not all improvements will be identified during this inspection.  Unexpected repairs should still be anticipated.  The inspection should not be considered a guarantee or warranty of any kind.

Please refer to the pre-inspection contract for a full explanation of the scope of the inspection.

Dry weather conditions prevailed at the time of the inspection.

The estimated outside temperature was 14 degrees F.

# Structure

## description of Structure

Foundation: 	(Masonry Block  (Masonry Block  (Steel

Floor Structure: 	(Wood Joist

Wall Structure: 	(Wood Frame, Brick Veneer

Ceiling Structure: 	(Not Visible

Roof Structure: 	(Not Visible

Ceiling Structure: 	(Joist

Roof Structure: 	(Roof Joists

## Structure observations

### recommendations / observations

## limitations of Structure inspection

As we have discussed and as described in your inspection contract, this is a visual inspection limited in scope by (but not restricted to) the following conditions:

- Structural components concealed behind finished surfaces could not be inspected.

- Only a representative sampling of visible structural components were inspected.

- Furniture and/or storage restricted access to some structural components.

- Engineering or architectural services such as calculation of structural capacities, adequacy, or integrity are not part of a home inspection.

Please also refer to the pre-inspection contract for a detailed explanation of the scope of this inspection.

# Roofing

## description of Roofing

Roof Covering: 	(Asphalt Shingle

Roof Flashings: 	(Metal

Chimneys: 	(Masonry

Roof Drainage System: 	(None

Method of Inspection: 	(Viewed with binoculars

## Roofing observations

### recommendations / observations

- Major Concern, Repair, Safety Issue:  The masonry chimney shows evidence of substantial deterioration. Rebuilding is needed to assure a safe and functional flue. The roof is leaking near chimney and needs to be evaluated by a contractor.

- Repair:  A rain cap and vermin screen should be installed on the masonry chimney and the chimney flue should be checked for damage. Damaged flues can be unsafe.

## limitations of Roofing inspection

As we have discussed and as described in your inspection contract, this is a visual inspection limited in scope by (but not restricted to) the following conditions:

- Not all of the underside of the roof sheathing is inspected for evidence of leaks.

- Evidence of prior leaks may be disguised by interior finishes.

- Estimates of remaining roof life are approximations only and do not preclude the possibility of leakage. Leakage can develop at any time and may depend on rain intensity, wind direction, ice build up, and other factors.

- Antennae, chimney/flue interiors which are not readily accessible are not inspected and could require repair.

- Roof inspection may be limited by access, condition, weather, or other safety concerns.

- Snow on the roof restricted the inspection.

Please also refer to the pre-inspection contract for a detailed explanation of the scope of this inspection.

# Exterior

## description of Exterior

Wall Covering: 	(Brick

Eaves, Soffits, And Fascias: 	(Aluminum  (Vinyl

Exterior Doors: 	(Solid Wood  (Vinyl-Covered

Entry Driveways: 	(Not visible due to snow

Entry Walkways And Patios: 	(Not visible due to snow

Porches, Decks, Steps, Railings: 	(Wood

Overhead Garage Door(s) Wood

## Exterior observations

### recommendations / observations

- Repair:  The exterior brickwork should be re-pointed (replacement of the mortar between the bricks) to prevent further deterioration.

- Major Concern, Monitor:  the detached garage is a low quality structure. With the exception of keeping the roof watertight and having functional gutters for roof water, it may not be worth investing in repairs. Rebuilding would be the better long term approach.

- Repair:  The windows require caulking.

- Monitor:  The driveway drain is  marginally adequate. Its performance should be carefully monitored during heavy rains. Care should be taken to maintain this drain free of debris. If problems develop, a large drain spanning the width of the driveway would be preferred. Drive runoff must be directed away from the building to avoid water entry/damage.

## limitations of Exterior inspection

As we have discussed and as described in your inspection contract, this is a visual inspection limited in scope by (but not restricted to) the following conditions:

- A representative sample of exterior components was inspected rather than every occurrence of components.

- The inspection does not include an assessment of geological, geotechnical, or hydrological conditions, or environmental hazards.

- Screening, shutters, awnings, or similar seasonal accessories, fences, recreational facilities, outbuildings, seawalls, break-walls, docks, erosion control and earth stabilization measures are not inspected unless specifically agreed-upon and documented in this report.

Please also refer to the pre-inspection contract for a detailed explanation of the scope of this inspection.

# Electrical

## description of Electrical

Size of Electrical Service: 	(120/240 Volt Main Service - Service Size: 100 Amps

Service Drop: 	(Overhead

Service Entrance Conductors: 	(Aluminum

Service Equipment &

Main Disconnects: 	(Breakers

Service Grounding: 	(Aluminum-Insulated

Sub-Panel(s): 	(Panel Rating: 100 Amp  (???  (Copper  (???  (Armored Cable "BX"  (Armored Cable "BX"

Ground Fault Circuit Interrupters: 	(None Found

Smoke Detectors: 	(None Found

## Electrical observations

### recommendations / observations

- Safety Issue:    The main panel cover plate (sometimes called the “Dead Front”) is missing. It should be replaced.

- Safety Issue:    Circuits within the main distribution panel that are doubled up (referred to as “double taps”) should be separated. Each circuit should be served by a separate fuse or breaker.

- Safety Issue:  The panel has homemade junction needs to be evaluated by a contractor

- Safety Issue:  All junction boxes should be fitted with cover plates, in order to protect the wire connections.

## limitations of Electrical inspection

As we have discussed and as described in your inspection contract, this is a visual inspection limited in scope by (but not restricted to) the following conditions:

- Electrical components concealed behind finished surfaces are not inspected.

- Only a representative sampling of outlets and light fixtures were tested.

- Furniture and/or storage restricted access to some electrical components which may not be inspected.

- The inspection does not include remote control devices, alarm systems and components, low voltage wiring, systems, and components, ancillary wiring, systems, and other components which are not part of the primary electrical power distribution system.

Please also refer to the pre-inspection contract for a detailed explanation of the scope of this inspection.

# Heating

## description of Heating

Energy Source: 	(Gas

Heating System Type: 	(Hot Water Boiler Buderus  2001

Vents, Flues, Chimneys: 	(Metal-Multi Wall

Heat Distribution Methods: 	(Baseboard Heaters

## Heating observations

### recommendations / observations

- Repair:  The heating system requires service. This should be a regular maintenance item to assure safe, reliable heat.

## limitations of Heating inspection

As we have discussed and as described in your inspection contract, this is a visual inspection limited in scope by (but not restricted to) the following conditions:

- The adequacy of heat supply or distribution balance is not inspected.

- The interior of flues or chimneys which are not readily accessible are not inspected.

- The furnace heat exchanger, humidifier, or dehumidifier, and electronic air filters are not inspected.

- Solar space heating equipment/systems are not inspected.

Please also refer to the pre-inspection contract for a detailed explanation of the scope of this inspection.

# Cooling / Heat Pumps

## description of Cooling / Heat Pumps

## Cooling / Heat Pumps observations

### recommendations / observations

## limitations of Cooling / Heat Pumps inspection

As we have discussed and as described in your inspection contract, this is a visual inspection limited in scope by (but not restricted to) the following conditions:

- Window mounted air conditioning units are not inspected.

- The cooling supply adequacy or distribution balance are not inspected.

- The air conditioning system could not be tested as the outdoor temperature was at or below 65 degrees F.

Please also refer to the pre-inspection contract for a detailed explanation of the scope of this inspection.

# Insulation / Ventilation

## description of Insulation / Ventilation

(Unknown  in Side Attic Areas

Roof Cavity Insulation: 	(Unknown in Cathedral Roof

Exterior Wall Insulation: 	(Not Visible

Basement Wall Insulation: 	(Not Visible

Crawl Space Insulation:

Roof Ventilation: 	(None Visible

Crawl Space Ventilation: 	(Exterior Wall Vents

Exhaust Fan/vent Locations: 	None

## Insulation / Ventilation observations

### recommendations / Energy saving Suggestions

## limitations of Insulation / Ventilation inspection

As we have discussed and as described in your inspection contract, this is a visual inspection limited in scope by (but not restricted to) the following conditions:

- Insulation/ventilation type and levels in concealed areas are not inspected. Insulation and vapor barriers are not disturbed and no destructive tests (such as cutting openings in walls to look for insulation) are performed.

- Potentially hazardous materials such as Asbestos and Urea Formaldehyde Foam Insulation (UFFI) cannot be positively identified without a detailed inspection and laboratory analysis.  This is beyond the scope of the inspection.

- An analysis of indoor air quality is not part of our inspection unless explicitly contracted-for and discussed in this or a separate report.

- Any estimates of insulation R values or depths are rough average values.

Please also refer to the pre-inspection contract for a detailed explanation of the scope of this inspection.

# Plumbing

## description of Plumbing

Water Supply Source: 	(Public Water Supply

Service Pipe to House: 	(Copper

Main Water Valve Location: 	(Side of house

Interior Supply Piping: 	(Copper

Waste System: 	(Public Sewer System

Drain, Waste, & Vent Piping: 	(Copper  (Cast Iron

Water Heater: 	(Tankless System Combined with Boiler  Buderus 2001

## Plumbing observations

### recommendations / observations

Repair:  No hot water on second floor.

- Deferred Cost Item:  The water heater is an old unit that may be approaching the end of its useful life. It would be wise to budget for a new unit. One cannot predict with certainty when replacement will become necessary.

## limitations of Plumbing inspection

As we have discussed and as described in your inspection contract, this is a visual inspection limited in scope by (but not restricted to) the following conditions:

- Portions of the plumbing system concealed by finishes and/or storage (below sinks, etc.), below the structure, or beneath the ground surface are not inspected.

- Water quantity and water quality are not tested unless explicitly contracted-for and discussed in this or a separate report.

- Clothes washing machine connections are not inspected.

- Interiors of flues or chimneys which are not readily accessible are not inspected.

- Water conditioning systems, solar water heaters, fire and lawn sprinkler systems, and private waste disposal systems are not inspected unless explicitly contracted-for and discussed in this or a separate report.

Please also refer to the pre-inspection contract for a detailed explanation of the scope of this inspection.

# Interior

## description of Interior

Wall And Ceiling Materials: 	(Plaster

Floor Surfaces: 	(Wood

Window Type(s) & Glazing: 	(Double/Single Hung

Doors: 	(Wood-Solid Core

## Interior observations

### recommendations / observations

- Monitor:  Insulation on the boiler and/or distribution piping may contain asbestos. This can only be verified by laboratory analysis. The Environmental Protection Agency (E.P.A.) reports that asbestos represents a health hazard if “friable” (damaged, crumbling, or in any state that allows the release of fibers). If replacement of the boiler necessitates the removal of the asbestos containing insulation, a specialist should be engaged. If any sections of this insulation are indeed friable, or become friable over time, a specialist should be engaged. Further guidance is available from the E.P.A. Due to the age of construction, there may be other materials within the home that contain asbestos but are not identified by this inspection report.

## limitations of Interior inspection

As we have discussed and as described in your inspection contract, this is a visual inspection limited in scope by (but not restricted to) the following conditions

- Furniture, storage, appliances and/or wall hangings are not moved to permit inspection and may block defects.

- Carpeting, window treatments, central vacuum systems, household appliances, recreational facilities, paint, wallpaper, and other finish treatments are not inspected.

Please also refer to the pre-inspection contract for a detailed explanation of the scope of this inspection.

# Appliances

## description of Appliances

## Appliances observations

Not Tested

### recommendations / observations

## limitations of Appliances inspection

As we have discussed and as described in your inspection contract, this is a visual inspection limited in scope by (but not restricted to) the following conditions

- Thermostats, timers and other specialized features and controls are not tested.

- The temperature calibration, functionality of timers, effectiveness, efficiency and overall performance of appliances is outside the scope of this inspection.

Please also refer to the pre-inspection contract for a detailed explanation of the scope of this inspection.

# Maintenance Advice

## upon taking ownership

After taking possession of a new home, there are some maintenance and safety issues that should be addressed immediately.  The following checklist should help you undertake these improvements:

- Change the locks on all exterior entrances, for improved security.

- Check that all windows and doors are secure.  Improve window hardware as necessary.  Security rods can be added to sliding windows and doors.  Consideration could also be given to a security system.

- Install smoke detectors on each level of the home.  Ensure that there is a smoke detector outside all sleeping areas.  Replace batteries on any existing smoke detectors and test them.  Make a note to replace batteries again in one year.

- Create a plan of action in the event of a fire in your home.  Ensure that there is an operable window or door in every room of the house.  Consult with your local fire department regarding fire safety issues and what to do in the event of fire.

- Examine driveways and walkways for trip hazards.  Undertake repairs where necessary.

- Examine the interior of the home for trip hazards.  Loose or torn carpeting and flooring should be repaired.

- Undertake improvements to all stairways, decks, porches and landings where there is a risk of falling or stumbling.

- Review your home inspection report for any items that require immediate improvement or further investigation.  Address these areas as required.

- Install rain caps and vermin screens on all chimney flues, as necessary.

- Investigate the location of the main shut-offs for the plumbing, heating and electrical systems.  If you attended the home inspection, these items would have been pointed out to you.

## regular maintenance

### every month

- Check that fire extinguisher(s) are fully charged.  Re-charge if necessary.

- Examine heating/cooling air filters and replace or clean as necessary.

- Inspect and clean humidifiers and electronic air cleaners.

- If the house has hot water heating, bleed radiator valves.

- Clean gutters and downspouts.  Ensure that downspouts are secure, and that the discharge of the downspouts is appropriate.  Remove debris from window wells.

- Carefully inspect the condition of shower enclosures.  Repair or replace deteriorated grout and caulk.  Ensure that water is not escaping the enclosure during showering.  Check below all plumbing fixtures for evidence of leakage.

- Repair or replace leaking faucets or shower heads.

- Secure loose toilets, or repair flush mechanisms that become troublesome.

### spring and fall

- Examine the roof for evidence of damage to roof coverings, flashings and chimneys.

- Look in the attic (if accessible) to ensure that roof vents are not obstructed.  Check for evidence of leakage, condensation or vermin activity.  Level out insulation if needed.

- Trim back tree branches and shrubs to ensure that they are not in contact with the house.

- Inspect the exterior walls and foundation for evidence of damage, cracking or movement.  Watch for bird nests or other vermin or insect activity.

- Survey the basement and/or crawl space walls for evidence of moisture seepage.

- Look at overhead wires coming to the house.  They should be secure and clear of trees or other obstructions.

- Ensure that the grade of the land around the house encourages water to flow away from the foundation.

- Inspect all driveways, walkways, decks, porches, and landscape components for evidence of deterioration, movement or safety hazards.

- Clean windows and test their operation.  Improve caulking and weather-stripping as necessary.  Watch for evidence of rot in wood window frames.  Paint and repair window sills and frames as necessary.

- Test all ground fault circuit interrupter (GFCI) devices, as identified in the inspection report.

- Shut off isolating valves for exterior hose bibs in the fall, if below freezing temperatures are anticipated.

- Test the Temperature and Pressure Relief (TPR) Valve on water heaters.

- Inspect for evidence of wood boring insect activity.  Eliminate any wood/soil contact around the perimeter of the home.

- Test the overhead garage door opener, to ensure that the auto-reverse mechanism is responding properly.  Clean and lubricate hinges, rollers and tracks on overhead doors.

- Replace or clean exhaust hood filters.

- Clean, inspect and/or service all appliances as per the manufacturer’s recommendations.

### annually

- Replace smoke detector batteries.

- Have the heating, cooling and water heater systems cleaned and serviced.

- Have chimneys inspected and cleaned.  Ensure that rain caps and vermin screens are secure.

- Examine the electrical panels, wiring and electrical components for evidence of overheating.  Ensure that all components are secure.  Flip the breakers on and off to ensure that they are not sticky.

- If the house utilizes a well, check and service the pump and holding tank.  Have the water quality tested.  If the property has a septic system, have the tank inspected (and pumped as needed).

- If your home is in an area prone to wood destroying insects (termites, carpenter ants, etc.), have the home inspected by a licensed specialist.  Preventative treatments may be recommended in some cases.

## Prevention is the best approach

Although we’ve heard it many times, nothing could be more true than the old cliché “an ounce of prevention is worth a pound of cure.”  Preventative maintenance is the best way to keep your house in great shape.  It also reduces the risk of unexpected repairs and improves the odds of selling your house at fair market value, when the time comes.

Please feel free to contact our office should you have any questions regarding the operation or maintenance of your home.  Enjoy your home!